## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Noida Metro Rail Corporation (NMRC) Limited
Name of Work: Design, engineering, manufacture, supply, Installation, testing and commissioning of , 1000KVA, 33KV/415V Compact Substation, Cabling and other accessories to be installed at NMRC station sector-51, Noida.
Contract No: NMRC/PD/CSS/196R/206/2022
Bidder Name :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE (inclusive of GST) In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Electrical Work | BI01010001010000000000000515BI0100001111 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | COMPACT SUBSTATION: | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.02 | Design, engineering, manufacture, testing and supply of Outdoor, Plinth Mounted, Compact Substation of 33KV/415 Volts, equipped with dry type 1000 KVA Cast Resin Transformer 33 KV Ring Main Unit consisting of 1 Nos. 33 KV SF6 Insulated Vacuum Circuit Breaker & with LT Air Circuit Breaker as secondary side complete as per as per standard & technical data sheet. | BI01010001010000000000000515BI0100001113 | 1 | SET. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.03 | Cabling | BI01010001010000000000000515BI0100001114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.04 | Supply of 1Cx120 Sq mm AL, XLPE power LSZH cable of 33 KV grade cable . | BI01010001010000000000000515BI0100001115 | 500 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.05 | Laying of one number XLPE power cable of 33 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.Upto 120 sq. mm | BI01010001010000000000000515BI0100001116 | 350 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.06 | Laying of one number XLPE power cable of 33 KV grade of following size in the existing masonry open duct as required..Upto 120 sq. mm | BI01010001010000000000000515BI0100001117 | 150 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.07 | Earthing: | BI01010001010000000000000515BI0100001118 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.08 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | BI01010001010000000000000515BI0100001119 | 1 | Sets |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.09 | Supply and burring of Safe Earthing Electrode T-39 (Hot-Dip Galvanized), Length up to 3000mm, outer pipe 76mm inner Dia 38mm terminal Dia 12 mm ,outer GI pipe of 16 SWG and inner GI pipe of 12 SWG with Hot Dip Galvanization up to 100 micron filled with crystalline conductive mixture (CCM) having anti corrosive & conductive property with 50 kgs activated soil (BFC) capable of reducing the soil resistivity with good mixture of retaining capacity along with 30cm square C.I. frame with hinged cover & masonary housing. (From electrode terminal to switch board, cost of 25 X 3 GI. Strip will be extra) Make: As approved in U.P. P.W.D., & C.P.R.I. Certified. | BI01010001010000000000000515BI0100001120 | 3 | Sets |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.1 | Providing and fixing 25 mm x 5 mm GI strip on surface or in recess for connection etc. as required. | BI01010001010000000000000515BI0100001121 | 50 | Meters |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.11 | Providing and fixing 50 mm x 5 mm GI strip on surface or in recess for connection etc. as required. | BI01010001010000000000000515BI0100001122 | 50 | Meters |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.12 | Cable Tray | BI01010001010000000000000515BI0100001123 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.13 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.225 mm width X 50 mm depth X 1.6 mm thickness | BI01010001010000000000000515BI0100001124 | 50 | Meters |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.14 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.225 mm width X 50 mm depth X 1.6 mm | BI01010001010000000000000515BI0100001125 | 4 | Each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.15 | Cable Termination | BI01010001010000000000000515BI0100001126 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.16 | Supply and installation of GIS termination kit suitable for single core 120 Sq mm AL, XLPE power LSZH cable of 33 KV grade. Make(Raychem, 3M or eq.) | BI01010001010000000000000515BI0100001127 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.17 | Supply and installation of gland for single core 120 Sq mm AL, XLPE power LSZH cable of 33 KV grade. | BI01010001010000000000000515BI0100001128 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.18 | Supply and installation of lugs ring type for single core 120 Sq mm AL, XLPE power LSZH cable of 33 KV grade. | BI01010001010000000000000515BI0100001129 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2 | Civil Work | BI01010001010000000000000515BI0100001131 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.01 | Surface dressing of the ground including removing vegetation and inequalities not exceeding 15 cm deep and disposal of rubbish, lead up to 50 m and lift up to 1.5 m. | BI01010001010000000000000515BI0100001132 | 25 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.02 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : | BI01010001010000000000000515BI0100001133 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.03 | 1:3:6 (1 Cement : 3 coarse sand (zone-III) : 6 graded stone aggregate 20 mm nominal size) | BI01010001010000000000000515BI0100001134 | 6.5 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.04 | Centering and shuttering including strutting, propping etc. and removal of form for | BI01010001010000000000000515BI0100001135 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.05 | Foundations, footings, bases of columns, etc. for mass concrete | BI01010001010000000000000515BI0100001136 | 10 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.06 | Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. | BI01010001010000000000000515BI0100001137 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.07 | All works upto plinth level Concrete of M25 grade with minimum cement content of 330 kg /cum | BI01010001010000000000000515BI0100001138 | 2.5 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.08 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. | BI01010001010000000000000515BI0100001139 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.09 | Thermo-Mechanically Treated bars of grade Fe-500D or more. | BI01010001010000000000000515BI0100001140 | 200 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information