## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: NOIDA METRO RAIL CORPORATION
Name of Work: Testing of Power Transformer(s), Relay(s) & equipment(s) callibration of NMRC Traction network for 2 years
Contract No: NMRC/PSI/TESTING/240/2023
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only)
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE (Including 18% GST) In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1.01 | 2-years Contract for Relay Testing, calibration of testing kits and Condition monitoring of 8 nos of Power Transformers installed in RSS(Sec-83 RSS & Sec-153 RSS) at Noida Metro Rail Corporation which comprehend 4 nos of Traction Transformer (132/25 kV, rating- 21.6/30 MVA ONAN/ONAF) 4 nos of Auxiliary Transformer (132/33 kV, rating- 10/15 MVA ONAN/ONAF) (There are 2 nos of Traction Transformers and 2 nos of Auxiliary Transformers in each RSS) | BI01010001010000000000000515BI0100001111 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.02 | General Points | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.03 | a)-Oil testing laboratory should be NABL accredited | BI01010001010000000000000515BI0100001113 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.04 | b)-The lab should also have IS-6855 accredited sampling procedure | BI01010001010000000000000515BI0100001114 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.05 | c)-Relay Test Kit:-3-phase secondary current injection test kit of OMICRON/ DOBEL/ Megger make | BI01010001010000000000000515BI0100001115 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.06 | d)-For testing the equipment like Transformer the contractor shall ensure readiness of equipment for testing ,however shutdown shall be provided by employer | BI01010001010000000000000515BI0100001116 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.07 | e)-Visit charge shall as per activity completion, material shall be provided by employer | BI01010001010000000000000515BI0100001117 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.08 | f)-In-case of breakdown the contractor engineer shall visit within 24 hours of reporting via call/sms/e-mail | BI01010001010000000000000515BI0100001118 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.09 | g)-Scope of testing of relays shall be as per tentative sample reports attached | BI01010001010000000000000515BI0100001119 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.01 | A-Detailed Scope of work for Conditioning Monitoring of Power Transformer(s) | BI01010001010000000000000515BI0100001120 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.02 | Measure of winding insulation resistance value of Power Transformer. (Measure IR at 60 sec & 10 sec) and calculate PI Index (IR at 60 sec/ IR at 10 sec.) (Scope- Testing, Periodicity- half yearly) | BI01010001010000000000000515BI0100001121 | 32 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.03 | Power Transformer Testing of Oil as per oil parameters- As per relevant IS- 1866 | BI01010001010000000000000515BI0100001122 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.04 | Oil Testing of Main Tank of Power Transformer:-which will include :-BDV (break Down Voltage); (Dissolve Gas Analysis:-Methane, Acetylene, Ethylene, Ethane, Hydrogen, Carbon Monoxide & Carbon Dioxiode); PPM (water content); Acidity (Neutralization Value); Resistivity(Specific Resitance), Dielectric Dissipiation Factor(Tan Delta) (Scope- Testing, Periodicity- half yearly) | BI01010001010000000000000515BI0100001123 | 32 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.05 | Oil Testing of OLTC of Power Transformer:- which will include :-BDV (break Down Voltage); (Dissolve Gas Analysis of gases :-Methane, Acetylene, Ethylene, Ethane, Hydrogen, Carbon Monoxide & Carbon Dioxiode); PPM (water content); Acidity (Neutralization Value; Resistivity(Specific Resitance), Dielectric Dissipiation Factor(Tan Delta) (Scope- Testing, Periodicity- half yearly) | BI01010001010000000000000515BI0100001124 | 48 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.06 | * Contractor has to submit the detail report analysis as well as trend analysis report of the Oil Test along with test report of testing from NABL accredited Lab | BI01010001010000000000000515BI0100001125 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.07 | Power Transformer Electrical Testing-As per relevant IS- 1866 | BI01010001010000000000000515BI0100001126 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.08 | Carry out Tan delta and capacitance measurement of bushing (of Power Transformer) and of windings (of power Transformer) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001127 | 16 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
2.09 | Magnetic balance test (Scope- Testing, Periodicity- As per requirement) | BI01010001010000000000000515BI0100001128 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.1 | Magnetic current test (Scope- Testing, Periodicity- As per requirement) | BI01010001010000000000000515BI0100001129 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.11 | Measurement of winding resistance at all taps (Scope- Testing, Periodicity- As per requirement) | BI01010001010000000000000515BI0100001130 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.12 | Measurement of voltage ratio at all taps (Scope- Testing, Periodicity- As per requirement) | BI01010001010000000000000515BI0100001131 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
2.13 | On line Partial Discharge measurement (Scope- Testing, Periodicity- As per requirement) | BI01010001010000000000000515BI0100001132 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
3.01 | Visit pertaining to any breakdown (Visit charge shall as per activity, material shall be provided by employer) (Scope- Visit, Periodicity- As per requirement) | BI01010001010000000000000515BI0100001133 | 12 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.01 | C-Testing of SIEMENS make relay(s) installed at various locations. | BI01010001010000000000000515BI0100001134 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
4.02 | 22 no. ASS | BI01010001010000000000000515BI0100001135 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
4.03 | 7SD80 (Line Differential) (testing parameters:- Differential Protection) (Annexure-A) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001136 | 192 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.04 | 7SR11 (O/C & Earth Fault) (testing parameters:- overcurrent and earth fault) (Annexure-B) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001137 | 100 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4.05 | 7SR12 (O/C & Earth Fault) (testing parameters:- overcurrent and earth fault) (Annexure-C) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001138 | 192 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.06 | 7ST61 (Distance Protection) (testing parameters:- Distance protection) (Annexure-D) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001139 | 8 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.07 | 2 no. RSS | BI01010001010000000000000515BI0100001140 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
4.08 | 7ST63 (Distance Protection)(testing parameters:-Over current, PFR(panto flashover),auto recloser,Distance,BCU,WPC) (Annexure-E) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001141 | 32 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.09 | 7SJ80 (Senstive earth fault/VDOC/50BF/ reverse power protection) (Annexure-F) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001142 | 48 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4.1 | 7SJ64 (BCU,Bay control unit protection132kV)( testing parameters:- Overcurrent, Earth Fault and Bay control Unit protection) (Annexure-G) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001143 | 56 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.11 | 7SD52 (Line Differential) (testing parameters :- Distance, Differential) (Annexure-H) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001144 | 32 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.12 | 7UT63 (Transformer Differential) (testing parameters:- Transformer Differential, tank earth fault, Restricted Earth Fault, buchholz,OTI,OSR,PRD Valve) (Annexure-I) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001145 | 32 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4.13 | 7SJ66 (O/C & Earth Fault)(Testing parameters:-over current, under voltage,BCU) (Annexure-J) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001146 | 96 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
4.14 | 7SS85 (Bus Bar protection) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001147 | 8 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.15 | 6MD85 (BCU( LT Side) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001148 | 8 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4.16 | Relay at incomer side of both RSS | BI01010001010000000000000515BI0100001149 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
4.17 | 7SD5/87 (Line Differential) (testing parameters:- differential protection) (Annexure-K) (Scope- Testing, Periodicity- Yearly) | BI01010001010000000000000515BI0100001150 | 16 | No.s |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.18 | **Tentative Performa of Relay testing for Relays mentioned above is attached from Annexure-A to Annexure-K | BI01010001010000000000000515BI0100001151 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
5.01 | D-Callibration of following testing kits from NABL accredited laboratory (Scope- Calibration, Periodicity- Yearly) | BI01010001010000000000000515BI0100001152 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
5.02 | Meggar (5kV) motwani make | BI01010001010000000000000515BI0100001153 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
5.03 | Hi-pot tester for cables upto 220kV level (technology products) | BI01010001010000000000000515BI0100001154 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
5.04 | Tan - Delta tester (shivnanda electronics) | BI01010001010000000000000515BI0100001155 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.05 | Primary injection kit, rated output of 3000A at 3V, 1500A at 6V and 750V at12V , motwani make | BI01010001010000000000000515BI0100001156 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
5.06 | Secondary injection kit with a continuously variable voltage of 0-250 VAC (capacity 2A) or 0-500VAC (capacity 1A), motwani make | BI01010001010000000000000515BI0100001157 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
5.07 | CT/PT accuracy tester (Udeyraj) | BI01010001010000000000000515BI0100001158 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.08 | Resonance circuit high voltage test kit (Applied techno products) | BI01010001010000000000000515BI0100001159 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
5.09 | Thermal imaging camera (Flir make) | BI01010001010000000000000515BI0100001160 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
5.1 | Cable fault detector (telemetrics equipments) | BI01010001010000000000000515BI0100001161 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.11 | Digital earth resistance meter (motwani make) | BI01010001010000000000000515BI0100001162 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
5.12 | Time interval meter (motwani make) | BI01010001010000000000000515BI0100001163 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
5.13 | Contact resistance meter (motwani make) | BI01010001010000000000000515BI0100001164 | 2 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information