## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.0 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: Noida Metro Rail Corporation (NMRC) Limited
Name of Work: Restoration contract for Civil, Electrical, Telecom works of NMRC Head Office.
Contract No: NMRC/CET/Restoration/159R/2021
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate (Inclusive of GST) in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [25 empty] | Specifications |  |  |  |  | TOTAL AMOUNT Without Tax Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | SCHDEULE A (CIVIL WORKS) | BI01010001010000000000000515BI0100001112 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.001 | Designing, fabricating, testing, installing and fixing in position Curtain Wall with Aluminium Composite Panel Cladding, with open grooves for linear as well as curvilinear portions of the building , for all heights and all levels etc. including:a) Structural analysis & design and preparation of shop drawings for pressure equalisation or rain screen principle as required, proper drainage of water to make it watertight including checking of all the structural and functional design. b) Providing, fabricating and supplying and fixing panels of aluminium composite panel cladding in pan shape in metalic colour of approved shades made out of 4mm thick aluminium composite panel material consisting of 3mm thick FR grade mineral core sandwiched between two Aluminium sheets (each 0.5mm thick). The aluminium composite panel cladding sheet shall be coil coated, with Kynar 500 based PVDF / Lumiflon based fluoropolymer resin coating of approved colour and shade on face # 1 and polymer (Service) coating on face # 2 as specified using stainless steel screws, nuts, bolts, washers, cleats, weather silicone sealant, backer rods etc. c) The fastening brackets of Aluminium alloy 6005 T5 / MS with Hot Dip Galvanised with serrations and serrated washers to arrest the wind load movement, fasteners, SS 316 Pins and anchor bolts of approved make in SS 316, Nylon separators to prevent bi-metallic contacts all complete required to perform as per specification and drawing The item includes cost of all material & labour component, the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working curtain wall with aluminium composite panel cladding, cleaning and protection of the curtain wall with aluminium composite panel cladding till the handing over of the building for occupation. Base frame work for ACP cladding is payable under the relevant aluminium item.s The Contractor shall provide curtain wall with aluminium composite panel cladding, having all the performance characteristics all complete, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineer-in-Charge. However, for the purpose of payment, only the actual area on the external face of the curtain wall with Aluminum Composite Panel Cladding (including width of groove) shall be measured in sqm. up to two decimal places. | BI01010001010000000000000515BI0100001113 | 12.84 | sqm | 3022.01 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.002 | DOOR AND WINDOWS Providing and fixing ISI marked flush door shutters conforming to IS: 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters : 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws. | BI01010001010000000000000515BI0100001114 | 15.23 | sqm | 1377.28 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.003 | Extra for providing lipping with 2nd class teak wood battens 25 mm minimum depth on all edges of shutters (over all area of door shutter to be measured) over item no. 9.20 and 9.21 | BI01010001010000000000000515BI0100001115 | 15.23 | sqm | 284.86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.004 | Providing & Fixing decorative high pressure laminated sheet of plain / wood grain in gloss / matt / suede finish with high density protective surface layer and reverse side of adhesive bonding quality conforming to IS : 2046 Type S including cost of adhesive of approved quality 1.0 mm thick. | BI01010001010000000000000515BI0100001116 | 199.92 | sqm | 542.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.005 | Providing and fixing aluminum die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | BI01010001010000000000000515BI0100001117 | 7 | each | 839.74 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.006 | Providing and fixing chromium plated handle with necessary screws etc. complete.125 mm | BI01010001010000000000000515BI0100001118 | 19 | each | 172.45 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.007 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacturer, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fittings, all complete as per direction of Engineer-in-charge (Door handle, lock and stopper etc.to be paid separately). | BI01010001010000000000000515BI0100001119 | 13.02 | sqm | 3836.28 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.008 | Providing and fixing approved brand and manufacturer SS 304 grade hardware's for Doors etc. Providing and fixing double action hydraulic floor spring of approved brand and manufacture conforming to IS : 6315 , having brand logo embossed on the body/ plate with double spring mechanism and door weight upto 125 kg, for doorsincluding cost of cutting floors ,embeding in floors as required and making good the same matching to the existing floor finishing and cover plates with brass pivot and single piece M.S. sheet outer box with slide plate etc. complete as per thedirection of Engineer-in-Charge. With stainless steel cover plate minimum 1.25 mm thickness. | BI01010001010000000000000515BI0100001120 | 10 | nos | 1651.39 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.009 | PARTITIONS AND WALL CLADDINGGYPSUM PARTITIONING:- Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing offrame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/sqm (both side inclusive), consisting of floor and ceiling channel 50mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as permanufacture's specification and direction of engineer in charge all complete.Providing & Fixing Full Height Glass partition using 12mmThk.Toughened glass partition complete with SS/ Alloy U channel at bottom of the floor and inside the ceiling as per manufacturer's specifications and to the satisfaction of the Engineer in charge. (For Measurement only Installed area will be considered).75 mm overall thickness partition with 12.5 mm thick double skin fire rated board confirming to is : 2095 : part I | BI01010001010000000000000515BI0100001121 | 17.65 | sqm | 1024.61 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.01 | Providing and fixing frame work for partitions/ wall lining etc. made of 50x50x1.6 mm hollow MS tube,placed along the walls, ceiling and floor in a grid pattern with spacing @ 60 cm centre to centre bothways (vertically & horizontally ) or at required spacing near opening, with necessary welding at junctions and fixing the frame to wall/ ceiling/ floors with steel dash fasteners of 8 mm dia, 75 mm longbolt, including making provision for opening for doors, windows, electrical conduits, switch boardsetc., including providing with two coats of approved steel primer etc. complete, all as per direction of Engineer-in-charge. | BI01010001010000000000000515BI0100001122 | 1496.38 | Kg | 72.88 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.011 | Providing & Fixing Full Height Glass partition using 12mmThk.Toughened glass partition complete with SS/ Alloy U channel at bottom of the floor and inside the ceiling as per manufacturer's specifications and to the satisfaction of the Engineer in charge. (For Measurement only Installed area will be considered). | BI01010001010000000000000515BI0100001123 | 23.49 | sqm | 2259.57 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.012 | FROSTED FILM (CRYSTAL QUALITY) :- Providing and fixing scotchcal over glass surface with 15 yrs MCS warranty) as approval of the Architect. (Only film surface area shall be measured and paid). | BI01010001010000000000000515BI0100001124 | 100.37 | sqm | 1968.74 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.013 | INSULATION- Providing and fixing thermal insulation with Resin Bonded rock wool conforming to IS: 8183, having density 48 kg/m3,50 mm thick,wrapped in 200 G Virgin Polythene Bags fixed to wall wirh screw, rawel plug & washers and held and in position by criss cossing GI wire etc. complete as per directions of Engineer-in-Charge. | BI01010001010000000000000515BI0100001125 | 192 | SQM | 264.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.014 | Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS : 15622, of approved make, in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand), including grouting the joints with white cement and matching pigments etc., complete.Size of Tile 600x600 mm | BI01010001010000000000000515BI0100001126 | 100 | sqm | 1146.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.015 | TILE GROUTING :- Grouting the joints of flooring tiles having joints of 3 mm width, using epoxy grout mix of 0.70 kg of organic coated filler of desired shade (0.10 kg of hardener and 0.20 kg of resin per kg), including filling/ grouting and finishing complete as per direction of Engineer-in-charge.Size of Tile 600x600 mm | BI01010001010000000000000515BI0100001127 | 265 | SQM | 147.64 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.016 | Providing and laying wooden flooring wit 1210 x 190 x 8mm thick pe laminated wooden pannels of vistroyal range including the cost of fixing PE sheet flush factor glue and bopp tape. The floor shall be provided with PE sheet than the PE sheet Shall be povided withflush factor foam sheet so as to naturalise load / weight effect on the flooring panels . The flooring panels shall be provided from top to tongened groove arrangement in flooring around . | BI01010001010000000000000515BI0100001128 | 220 | sqm | 3036.54 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.017 | CEILING GYPBOARD CEILING :- Providing and fixing false ceiling at all height including providing and fixing of frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) as per IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mm thick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, one flange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with 6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50 mm of required length with nuts & bolts of required size and other end of angle hanger fixed with intermediate G.I. channels 45x15x0.9 mm running at the spacing of 1200 mm centre to centre, to which the ceiling section 0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm each having lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in a direction perpendicular to G.I. intermediate channel with connecting clips made out of 2.64 mm dia x 230 mm long G.I. wire at every junction, including fixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20 mm and 30 mm long. Including jointing and finishing to a flush finish oftapered and square edges of the board with recommended jointing compound , jointing tapes , finishing with jointing compound in 3 layers covering upto 150 mm on both sides of joint and two coats of primer suitable for board, all as per manufacturer's specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed, all complete as per drawings, specification and direction of the Engineer in Charge but excluding the cost of painting with :12.5 mm thick tapered edge gypsum plain board conforming to IS: 2095- Part I | BI01010001010000000000000515BI0100001129 | 650 | SQM | 657.92 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.018 | Providing and Applying plaster of Paris putty of 2mm thickness over Plastered surface to prepare the surface even and smooth complete | BI01010001010000000000000515BI0100001130 | 200 | sqm | 82.53 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.019 | Finishing walls with textured exterior paint of required shade : New work (Two or more coats applied @ 3.28 ltr/10 sqm) over and including priming coat of exterior primer applied @ 2.20kg/10 sqm. | BI01010001010000000000000515BI0100001131 | 25.43 | sqm | 103.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Finishing walls with textured exterior paint of required shade :with water thinable cement primer on wall surface having VOC content less than than 50 grams/ litre | BI01010001010000000000000515BI0100001132 | 750 | sqm | 25.79 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.021 | Wall painting with premium acrylic emulsion paint of interior grade, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre. of Approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour. Two coats. | BI01010001010000000000000515BI0100001133 | 812.84 | sqm | 57.84 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.022 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edge to give high gloss finish etc. complete at all levels. Granite of any colour and shadeArea of Slab over 0.50sqm | BI01010001010000000000000515BI0100001135 | 17.65 | sqm | 3081.73 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.023 | Extra for providing edge moulding to 18mm thick marble stone counters, Vanities etc. including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge.Granite work. | BI01010001010000000000000515BI0100001136 | 37.8 | metre | 172.21 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.024 | Extra for providing opening of required size & shape for wash basins/ kitchen sink in kitchen platform, vanity counters and similar location in marble/Granite/stone work including necessary holes for pillar taps etc. including rubbing and polishing of cut edges etc. complete. | BI01010001010000000000000515BI0100001137 | 2 | each | 286.78 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.025 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metreslead. Dismantling tile work in floors and roofs laid incementmortar including stacking material within 50 metreslead. For thickness of tiles above 25 mm and up to 40 mm | BI01010001010000000000000515BI0100001138 | 180 | Sqm | 32.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.026 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead: Of area 3 sq. metres and below | BI01010001010000000000000515BI0100001139 | 25 | nos | 104.48 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.027 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer in-charge, beyond 50 m initial lead, for all leads including all lifts involved.Lime, murrum, building rubbish upto 30 kms | BI01010001010000000000000515BI0100001140 | 50 | Cum | 101.25 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.028 | SUBHEAD - II : COLD / FLUSHING WATER SUPPLY (INTERNAL / EXTERNAL): Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having Thermal stability for hot & cold water supply, including all CPVC plain &brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineerin Charge.. 20 mm nominal outer dia Pipes | BI01010001010000000000000515BI0100001141 | 20 | RM | 198.69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.029 | SUBHEAD - II : COLD / FLUSHING WATER SUPPLY (INTERNAL / EXTERNAL): Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having Thermal stability for hot & cold water supply, including all CPVC plain &brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineerin Charge.. 25 mm nominal outer dia Pipes | BI01010001010000000000000515BI0100001142 | 20 | RM | 243.57 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.03 | SUBHEAD - II : COLD / FLUSHING WATER SUPPLY (INTERNAL / EXTERNAL): Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having Thermal stability for hot & cold water supply, including all CPVC plain &brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineerin Charge..32 mm nominal outer dia Pipes | BI01010001010000000000000515BI0100001143 | 20 | RM | 293.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.031 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and thebase support for tank. | BI01010001010000000000000515BI0100001144 | 2000 | liters | 4.99 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.032 | Providing and fixing of copper connection 450 mm long including nuts and washers and making connection to fixtures and fittings complete as required.(Make-Jaquar-Model-ALD-805B ) | BI01010001010000000000000515BI0100001145 | 10 | Nos. | 259.97 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.033 | Diluting and injecting chemical emulsion for POST- CONSTRUCTIONAL anti-termite treatment (excluding the cost of chemical emulsion) : Treatment of existing masonry using chemical emulsion @ one litre per hole at 300 mm interval including drilling holes at 45 degree and plugging them with cement mortar 1:2 (1 cement : 2 coarse sand) to the full depth of the hole : With Chlorpyriphos/Lindane E.C. 20% with 1% concentration | BI01010001010000000000000515BI0100001146 | 100 | RMT. | 14.31 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.034 | Supplying chemical emulsion in sealed containers including delivery as specified. Chlorpyriphos / Lindane emulsifiable concentrate of 20% | BI01010001010000000000000515BI0100001147 | 100 | litre | 152.01 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.035 | Providing wood work in frames of doors, windows, clerestory windows and other frames, wrought framed and fixed in position with hold fast lugs or with dash fasteners of required dia & length ( hold fast lugs or dash fastener shall be paid for separately). Second class teak wood | BI01010001010000000000000515BI0100001148 | 0.5 | Cum | 74798.72 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.036 | Repairs to plaster of thickness 12 mm to 20 mm in patches of area 2.5 sq meters and under, including cutting the patch in proper shape, raking out joints and preparing and plastering the surface of the walls complete, including disposal of rubbish to the dumping ground within 50 metres lead: With cement mortar 1:4 (1 cement : 4 fine sand) | BI01010001010000000000000515BI0100001149 | 100.35 | Sqm | 202.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.037 | Providing and fixing thermal insulation of ceiling (under deck insulation) with Resin Bonded Rockwool conforming to IS: 8183,density 48 kg/m3, 50 mm thick, wrapped in 200 G Virgin Polythene bags fixed to ceiling with metallic cleats (50x50x3 mm) @ 60 cm and wire mesh of 12.5mm x 24 gauge wire mesh, for top most ceiling of building. | BI01010001010000000000000515BI0100001150 | 323.78 | SQM | 401.07 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.038 | Providing and fixing double scaffolding system (cup lock type) on the exterior side of building/structure, upto 25 metre height, above ground level, including additional rows of scaffolding in stepped manner as per requirement of site, made with 40 mm dia M.S. tube, placed 1.5 metre centre to centre, horizontal & vertical tubes joint with cup & lock system with M.S. Tubes, M.S. tube challis, M.S. clamps and staircase system in the scaffolding for working platform etc. and maintaining it in a serviceable condition for execution of work of cleaning and/ or pointing and/ or applying chemical and removing it thereafter. The scaffolding system shall be stiffened with bracings, runners, connecting with the building etc, wherever required, if feasible, for inspection of work at required locations with essential safety features for the workmen etc., complete as per directions and approval of Engineer-in-charge. Note:- (1) The elevational area of the scaffolding shall be mesured for payment purpose. (2) The payment will be made once only for execution of all items of such works. | BI01010001010000000000000515BI0100001151 | 150 | SQM | 130.72 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.039 | Providing and fixing plywood 4 mm thick, one side decorative veneer conforming to IS: 1328 (type-1), for plain lining / cladding with necessary screws, including priming coat on unexposed surface with : Decorative veneer facings of approved manufacture. Approved Make:- Greenlame/Century/Merino | BI01010001010000000000000515BI0100001152 | 393.11 | Sqm | 945.19 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.04 | Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll from G.I. sheet with zinc coating of 120 gms/sqm (both side inclusive), consisting of floor and ceiling channel 50mm wide having equal flanges of 32mm and 0.50mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm lenght or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having ond flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mmm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each ) to be provided at the orizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners ( 25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete. 75 mm overall thickness partition with 12 mm commercial ply over 6 mm thick ply both side | BI01010001010000000000000515BI0100001153 | 80 | Sqm | 3224.87 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.041 | Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll from G.I. sheet with zinc coating of 120 gms/sqm (both side inclusive), consisting of floor and ceiling channel 50mm wide having equal flanges of 32mm and 0.50mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm lenght or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having ond flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mmm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each ) to be provided at the orizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners ( 25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete. 75 mm overall thickness partition with 12 mm commercial ply over 6 mm thick ply in one side and another side 12.5 mm thick tapered edge gypsum fire resistant board. | BI01010001010000000000000515BI0100001154 | 20 | Sqm | 2062.63 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.042 | Providing, and fixing S.S.316 GradeDoor Stop Half Moon[Finish : Satin] of approved quality with necessary screws etc. complete. Approved Make:- Kich/Hafele/ Godrej | BI01010001010000000000000515BI0100001155 | 6 | Nos | 477.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.043 | Providing, and fixing SS 316 Pull Handle with lock Ø 38mm X 1125mm (C/C)X1500mm(L) of approved quality with necessary screws etc. complete.Approved Make:- Kich/Hafele/ Godrej | BI01010001010000000000000515BI0100001156 | 8 | Nos | 12100.51 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.044 | Providing, and fixing SS 316 Door Hinge with 2 Ball Bearing (100X75X3)mm including SS Screws [PR Series] [Satin]of approved quality with necessary screws etc. complete. Approved Make:- Kich/Hafele/ Godrej | BI01010001010000000000000515BI0100001157 | 12 | Nos | 529.93 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.045 | Providing, and fixing Soft Closing Clip on Hinge (Inset) [Finish: Satin] of approved quality with necessary screws etc. complete. Approved Make:- Kich/Hafele/ Godrej | BI01010001010000000000000515BI0100001158 | 100 | Nos | 369.57 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.046 | Providing and fixing Lock Body 9" [With Stainless Steel Main and strike Plate] of approved quality with necessary screws etc. complete. Approved Make:- Kich/Hafele/ Godrej | BI01010001010000000000000515BI0100001159 | 12 | Nos. | 745.12 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.047 | Providing and fixing Cylinder-60 mm [key & knob] [Fire Rated- BSEN 1634 : 1 : 2000 Certified] of approved quality with necessary screws etc. complete. Approved Make:- Kich/Hafele/ Godrej | BI01010001010000000000000515BI0100001160 | 12 | Nos. | 701.92 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.048 | Providing and fixing SS 316 Grade Mortice Handle ▫ 19mm+duro profile escutcheons [Satin][BSEN 1906-2010 Tested] with screws etc. complete. Approved Make:- Kich/Hafele/ Godrej | BI01010001010000000000000515BI0100001161 | 12 | Nos. | 2086.96 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.049 | Providing and fixing SS 304 Grade Tower Bolt (Square) Size: 300mm Finish: Satin with necessary screws etc. complete. Approved Make:- Kich/Hafele/ Godrej 250x10 mm | BI01010001010000000000000515BI0100001162 | 12 | Nos. | 649.57 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.05 | Providing and fixing factory made uPVC white color sliding glazed window upto 1.8m in height, dimension comprising of uPVC multi-chambered extruded frame and sash profiles, Frame should be duly reinforced with 1mm G.I. section & Sash with 1.5 to 2mm thick G.I. section based on wind load calculation, (shape & size according to uPVC profile), appropriate dimension of uPVC extruded glazing beads, uPVC extruded interlocks, and uPVC extruded interlocks, and uPVC extruded inline sash adaptor (if required), Co-extruded TPV Gasket having separate dranage sysem, wool pile, zincalloy (white powder coated) handle on one side of extreme panel along with zinc plated mildsteel multi locking having transmission gear with keeps, zinc alloy (white powder coated) touchlocks with hook, (if required for wire mesh panel) stainless steel (SS 304 grade) body with adjustable douoble bylon rollers (weight bearing capacity to be 120kg), G.I. Fasteners 100x8 mm size for fixing frame to finished wall, plastic packers, plastic caps and necessary steel screws etc. Profile of Frame & sash shall be metered cut and fusion welded at all corner. including drilling of holes for fixing hardware & drainage etc. After fixing frame, the gap between frame and adjacent wall shall be filled with PU foam / backer rod of required size and the approved quality. After that sealed with weather proof silicon sealant at both the side (inside & outside), all complete as per approved drawing and direction of Engineer-in-charge. NOTE- For uPVC frame sash & mullioin extruded profile minus 5% tolerance in dimension i.e. in depth & width of profile shall be acceptable. Three track five panels sliding cum fixed windows out of them one is completely fixed at centre & two sliding glass panels along with two nos fly proof SS wire mesh panel (two nos glazed & two nos wire mesh panel) made of frame 108x45 mm & sash 39x58 mm & screen sash 39x58 mm, all having wall thickness of 2.2+0.2 mm single glazing bead 20x18mm & necessary interlock of appropriate dimensiion. Glass:- 6mm Tooughened. Approved Make:- Wintech/ Aluplast/Fenesta/EuroGroup | BI01010001010000000000000515BI0100001163 | 50 | sQm | 8553.72 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.051 | Providing and fixing factory made uPVC white colour casement/ Casement cumfixed glazed door comprising of uPVC multi-chambered frame, sash and mullion(where ever required) extruded profiles duly reinforced with 1.60 ± 0.2 mm thickgalvanized mild steel section made from roll forming process of required length(shape & size according to uPVC profile), uPVC extruded glazing beads ofappropriate dimension, EPDM gasket, zinc alloy (white powder coated) 3D hingesand one handle on each side of panels along with zinc plated mild steel multipoint locking having transmission gear, cylinder with keeps and one side key,G.I fasteners 100 x 8 mm size for fixing frame to finished wall and necessarystainless steel screws, etc. Profile of frame & sash shall be mitred cut and fusionwelded at all corners, mullion (if required) shall be also fusion welded includingdrilling of holes for fixing hardware's and drainage of water etc. After fixingframe the gap between frame and adjacent finished wall shall be filled withweather proof silicon sealent over backer rod of required size and of approved quality, all complete as per approved drawing & direction of Engineer-in-Charge.(Single / double glass panes and silicon sealent shall be paid separately).Note: For uPVC frame, sash and mullion extruded profiles minus 5% tolerancein dimension i.e. in depth & width of profile shall be acceptable.Casement door with 3D hinges made of (big series) frame 60 x 55 mm & sash 60x 102 mm both having wall thickness of 2.3 ± 0.2 mm and single glazing bead /double glazing bead of appropriate dimension. (Area of door upto 2.00 sqm).Glass : - 6mm Toughened Saint Gobain Approved Make:- Kich/Hafele/ Godrej | BI01010001010000000000000515BI0100001164 | 9 | SQM | 8891.63 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.052 | Providing and fixing in wall lining on layer of the 12 mm thick commercial ply over second layer 6 mm thick commercial ply including necessary groves and fixing arrangement over ms frame as per drawing and direction of E/I MS frame shall be paid separately. | BI01010001010000000000000515BI0100001165 | 270 | SQM | 1784.15 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.053 | Providing and fixing S.S. 304 Grade Cupboard Lock Size : 25mm [finish: Satin] of approved quality including necessary screws etc. complete. Approved Make:- Kich/Hafele/ Godrej | BI01010001010000000000000515BI0100001166 | 20 | NOS | 544.05 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.054 | Providing and fixing mineral fibre false ceiling tiles at all heights of size 595X595mm (dune) of approved texture, design and pattern. The tiles should have Humidity Resistance (RH) of 99%, Light Reflectance ?85%, Thermal Conductivity k = 0.052 - 0.057 w/m K, Fire Performance as per (BS 476 pt - 6&7)in true horizontal level suspended on interlocking T-Grid (DC Flexzone Silhouette slotted tee) of hot dipped allround galvanized iron section of 0.33 mm thick (galvanized @120 gsm )comprising of main T runners of 15x32 mm of length 3000 mm, cross T of size 15x32mm of length 1200 mm and secondary intermediate cross T of size 15x32 mm of length 600 mm to form grid module of size 600x600 mm suspended from ceiling using galvanized mild steel item (galvanised@80gsm) 50 mm long 8mm outer diameter M-6 dash fasteners, 6 mm diameter fully threaded hanger rod up to 1000 mm length and L-shape level adjuster of size 85x25x2 mm, spaced at 1200 mm centre to centre along main ‘T’. The system should rest on periphery walls /partitions with the help of GI perimeter wall angle of size24x24X3000 mm made of 0.40 mm thick sheet, to be fixed to the wall with help of plastic rawl plug at 450 mm centre to centre & 40 mm long dry wall S.S. screws. The exposed bottom portion of all T-sections used in false ceiling support system shall be pre-painted with polyester baked paint, for all heights. The work shall be carried out as per specifications, drawings and as per directions of the engineer-in-charge. With 16 mm thick beveled tegular mineral fibre false ceiling tile (NRC 0.55 to 0.6) Approved Make:- Armstrong/Anatone | BI01010001010000000000000515BI0100001167 | 60 | SQM | 1422.84 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.055 | Providing and fixing plain lining with necessary screws/nuts & bolts/ nails,including a coat of approved primer on one face, and fixed on wooden /steel frame work, complete as per direction of Engineer-incharge (Framework shall be paid for separately). 12mm thick commercial ply conforming to IS : 1328 BWR typeincluding a coat of approved primer on one face, and fixed on wooden /steel frame work, complete as per direction of Engineer-incharge (Framework shall be paid for separately). 12mm thick commercial ply conforming to IS : 1328 BWR type | BI01010001010000000000000515BI0100001168 | 60 | sqm | 865.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.056 | Providing and fixing 18mm thk AGL make Ultra White composite marble. Make is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001169 | 3.5 | sqm | 7141 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.057 | P/ f partition upto ceiling height consisting of G.I. frame and required board 75 mm overall thickness partition with 12 mm commercial ply in one side and another side 12.5 mm thick tapered edge gypsum fire resistant board. | BI01010001010000000000000515BI0100001170 | 12 | sqm | 1690.66 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.058 | P/ f partition upto ceiling height consisting of G.I. frame and required board 75 mm overall thickness partition with 12 mm commercial ply in both side | BI01010001010000000000000515BI0100001171 | 33 | sqm | 2446.05 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.059 | P/ A of Melamine polish including cost of PU Coating on wood surface by compressor Make is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001172 | 410 | sqm | 1487 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.06 | Providing and fixing 18 mm thick, 150 mm wide pelmet.Make is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001173 | 45 | Metre | 678.83 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.061 | Providing and fixing of Teak Wood door Cover moudling including melamine polishing etc., complete in all respect size 50x25 mm | BI01010001010000000000000515BI0100001174 | 35 | Metre | 188.76 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.062 | Providing and fixing of TEAK WOOD DESIGNER MOULDING 38X15MM WITH GROOVE including melamine polishing etc., complete in all respect | BI01010001010000000000000515BI0100001175 | 135 | Metre | 204.94 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.063 | Providing and fixing of 1mm thick LAMINATE DECORATIVE SPECIAL EDITION | BI01010001010000000000000515BI0100001176 | 25 | SQM | 840.26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.064 | Providing and fixing 50 mm wide X 75MM HIGH Boxing for Fixed Glass made out of 18MM THICK COMMERCIAL BOARD WITH 1MM THICK LAMINATE BOTH SIDE, fixing with rawl plugs 100 mm long etc. all complete | BI01010001010000000000000515BI0100001177 | 15 | Metre | 895.63 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.065 | Extra for design for wall ,designer grooves with horizontal and vertical complete in all respect | BI01010001010000000000000515BI0100001178 | 350 | sqm | 471.09 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.066 | FIXED FURNITURE Cabinet Carcass- Providing and fixing Pre-laminated 18mm thick Commercial Ply, with one side decorative and other side balancinglamination Grade I, Type II exterior grade IS : 12823 marked, in cabinet carcass with screws and fittings wherever required, edges to be painted with polyurethane primer (fittings to be paid separately). | BI01010001010000000000000515BI0100001179 | 120 | Sqm | 2835.71 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.067 | Supply and Installlation of Roller Blinds without head rail of approved shade and color. Suggested Brand: VISTA | BI01010001010000000000000515BI0100001180 | 50 | sqm | 1834.69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.068 | Providing and laying Upvc 90 mm dia pipe Make is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001181 | 20 | Metre | 189.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.069 | Providing and laying Upvc 110 mm dia pipe.Make is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001182 | 20 | Metre | 269.96 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.07 | Providing and laying Upvc 160 mm dia pipe.Make is as per direction of Engineer-in-charge] | BI01010001010000000000000515BI0100001183 | 20 | Metre | 553 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.071 | P/F110 mm dia UPVC Door Bend, having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001184 | 2 | Each | 124 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.072 | P/F 110 mm dia UPVC Plain Bend, having thermal stability for hot & cold water supply | BI01010001010000000000000515BI0100001185 | 2 | Each | 183 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.073 | P/F 110 mm dia UPVC Door "T", having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001186 | 2 | Each | 156 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.074 | P/F 110 mm dia UPVC Plain "T", having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001187 | 2 | Each | 227 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.075 | P/F 110 mm dia UPVC Naini Trap, having thermal stability for hot & cold water supply | BI01010001010000000000000515BI0100001188 | 2 | Each | 140 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.076 | P/F 160 mm dia UPVC Door Bend, having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001189 | 2 | Each | 302 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.077 | P/F 160 mm dia UPVC Plain "T", having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001190 | 2 | Each | 410 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.078 | P/F 160 mm dia UPVC Plain Bend, having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001191 | 2 | Each | 194 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.079 | P/F 160 mm dia UPVC End Cap, having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001192 | 2 | Each | 146 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.08 | P/F 90 mm dia UPVC Door Bend, having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001193 | 2 | Each | 156 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.081 | P/F 90 mm dia UPVC Plain Bend, having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001194 | 2 | Each | 124 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.082 | P/F 90 mm dia UPVC Door "T", having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001195 | 2 | Each | 200 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.083 | P/F 90 mm dia UPVC Plain "T", having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001196 | 2 | Each | 146 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.084 | P/F 110 mmx90mm dia UPVC Naini Trap, having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001197 | 2 | Each | 151 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.085 | P/F 110 mm dia UPVC Cowl, having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001198 | 2 | Each | 167 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.086 | P/F 90 mm dia UPVC Cowl, having thermal stability for hot & cold water supply. | BI01010001010000000000000515BI0100001199 | 2 | Each | 140 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.087 | P/L vitrified floor tiles in different sizes of approved make Size of Tile 120x60 cm | BI01010001010000000000000515BI0100001200 | 150 | sqm | 1791.25 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.088 | Providing and laying rectified Glazed Ceramic floor tiles of size 300x300mm or more (thickness to be specified by the manufacturer), of 1st quality conforming to IS : 15622, of approved make, in colours White,Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4(1 Cement: 4 Coarse sand), jointing with grey cement slurry @ 3.3 kg/sqm including grouting the joints with white cement and matchingpigments etc., complete. | BI01010001010000000000000515BI0100001201 | 15 | SQM | 776.66 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.089 | Providing and fixing 28mm thick imported wooden seasoned and chemically treated Wall clading including base frame of 50x25mm aluminium section with inside fill hardwood section 48x23 mm finished of required size with necessary connecting brackets, screws , etc ( cost of polising paid seprately) | BI01010001010000000000000515BI0100001202 | 55 | SQM | 5277 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.09 | Supplying and placing hanging planter box in the size of 300mm X 250mm X 450mm - 2nos. made out of 26mm thick imported wooden seasoned and chemically treated , Steel with painting, etc. including cost of ms frame workDouble hanging planter | BI01010001010000000000000515BI0100001203 | 2 | SET | 8500 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.091 | Providing and fixing 12 mm thick transparent multi wall poly carbonate sheet partition with ss 304 grade patch connector of approved brand and manufacture ( cost of SS Frame paid seprately) | BI01010001010000000000000515BI0100001204 | 6.26 | SQM | 1608 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.092 | Providing and fixing of CNC CUT DESIGN WPC - Wood Polimer Composite Boards are made from 70% of virgin polymer, 15% of wood powder and rest 15% of additives and requisite chemicals (0% Harmfull Chemicals). As per approved designs | BI01010001010000000000000515BI0100001205 | 5.65 | SQM | 3435 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.093 | Providing and fixing of Artificial Grass 40 mm thick, composion made out of UV Resistant Polyethylene and Polypropylene Blend, with Straight and Curly Mono filament Yarn, pile weight 1,160Gr/Sq.m, backing WovenPolypropylenewithFibrelockedFleeceandLatexCompound | BI01010001010000000000000515BI0100001206 | 70 | SQM | 1000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.094 | Providing and fixing of VISTA MAKE rectreble awning systems with fabric complete in all respect | BI01010001010000000000000515BI0100001207 | 15.33 | SQM | 5210 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.095 | Providing and fixing of 6mm thick laquard glass as per approved design | BI01010001010000000000000515BI0100001208 | 16.86 | SQM | 6165 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.096 | Providing and fixing of 100mm thick 42 mm density Cushion with leatherite for seating module as per approved colour | BI01010001010000000000000515BI0100001209 | 0.75 | SQM | 4714 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.097 | Providing and fixing of Printed Glass with approved design | BI01010001010000000000000515BI0100001210 | 18.29 | SQM | 8500 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.098 | Providing and fixing of Customised wooden Name plate with 6 mm thick transparent acrylic sheet as per approved design including cost of melamine polishing complete in all respect | BI01010001010000000000000515BI0100001211 | 4 | NOS | 1168 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.099 | Providing and fixing of Various painting | BI01010001010000000000000515BI0100001212 | 1 | LOT | 18122 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.1 | Applying of groove Polishing on wall panelling/partition | BI01010001010000000000000515BI0100001213 | 1000 | RM | 25 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | SCHDEULE B (ELECTRICAL WORKS) | BI01010001010000000000000515BI0100001214 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.001 | Providing and fixing plain 16/0.20mm (0.50sqmm) twin flat flexible, FRLS PVC insulated, copper conductor cable, in PVC sleeve of suitable size on the floor/ wall, or side of the table/ door etc. as required. | BI01010001010000000000000515BI0100001215 | 5 | meter | 22.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.002 | Wiring for light point / fan point / exhaust fan point / call bell point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface / recessed Medium class PVC conduit with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc as required - Group C | BI01010001010000000000000515BI0100001216 | 175 | Point | 586.97 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.003 | Wiring for light / power plug with 2 x 4 sq. mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit along with 1 No. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | BI01010001010000000000000515BI0100001217 | 539.9 | Metre | 132.44 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.004 | Wiring for circuit / submain alongwith earth wiring with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface / recessed in suitable size of steel conduit as required. 2 x 2.5 sq. mm + 1 x 2.5 sq. mm earth wire | BI01010001010000000000000515BI0100001218 | 1507.6 | Metre | 107.09 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.005 | Wiring for circuit / submain alongwith earth wiring with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface / recessed in suitable size of steel conduit as required. 2 x 4 sq. mm + 1 x 4 sq. mm earth wire | BI01010001010000000000000515BI0100001219 | 232 | Metre | 132.44 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.006 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | BI01010001010000000000000515BI0100001220 | 111 | Each | 247.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.007 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | BI01010001010000000000000515BI0100001221 | 50 | Each | 322.91 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.008 | Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface / recessed steel / PVC conduit as required. | BI01010001010000000000000515BI0100001222 | 342.8 | Metre | 22.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.009 | Supplying and fixing of following sizes of steel conduit along with accessories in surface / recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. 25 mm | BI01010001010000000000000515BI0100001223 | 253.06 | Metre | 116.09 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.01 | Supplying and Fixing following sizes / modules , GI box along with modular base & cover plate for modular switches in recess etc as required. 1 or 2 Module (75mmX75mm) | BI01010001010000000000000515BI0100001224 | 17 | Each | 135.71 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.011 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required | BI01010001010000000000000515BI0100001225 | 12 | Each | 18.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.012 | Providing and laying 1.6 MM thick AL factory fabricated raceways of the following sizes including providing removable 3 mm thick GI cover knock out holes and fixing accessories earthing with 8 SWG copper earth wire at ends complete as required including floor supports, bends, access boxes and tap off boxes as per specification and cross over as per site requirement. 250 mm wide x 40 mm deep raceway | BI01010001010000000000000515BI0100001226 | 43.06 | RM | 1650.53 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.013 | Providing and laying 1.6 MM thick AL factory fabricated raceways of the following sizes including providing removable 3 mm thick GI cover knock out holes and fixing accessories earthing with 8 SWG copper earth wire at ends complete as required including floor supports, bends, access boxes and tap off boxes as per specification and cross over as per site requirement. 100 mm wide x 40 mm deep raceway | BI01010001010000000000000515BI0100001227 | 104.21 | RM | 696.51 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.014 | SECTION - II - DISTRIBUTION BOARD Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 2 + 12 way, Double door | BI01010001010000000000000515BI0100001228 | 1 | Each | 1098.72 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.015 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 6 way (4 + 18), Double door | BI01010001010000000000000515BI0100001229 | 4 | Each | 2154.93 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.016 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 8 way (4 + 24), Double door | BI01010001010000000000000515BI0100001230 | 1 | Each | 2573.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.017 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | BI01010001010000000000000515BI0100001231 | 186 | Each | 174.62 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.018 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 25 A | BI01010001010000000000000515BI0100001232 | 4 | Each | 1927 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.019 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40A | BI01010001010000000000000515BI0100001233 | 9 | Each | 2095 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.02 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63A | BI01010001010000000000000515BI0100001234 | 3 | Each | 2640 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.021 | Supplying and fixing 20 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 A "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | BI01010001010000000000000515BI0100001235 | 5 | Each | 780 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.022 | Supply and fixing of recess mounting round Ceilling cutout 160 mm height 55 mm 18 Watt LED Down Lighter having Powder coated die cast aluminium housing with heat sink, diffuser/ Reflector and driver set complete in all respect CAT-AAA | BI01010001010000000000000515BI0100001236 | 97 | Nos. | 2158.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.023 | Supply and fixing of recess / surface / pendent mounting round 6 to 8 watt LED Light fixture having powder coated die cast aluminium housing with heat sink, diffuser and driver set complete in all respects. (Philips Cat no. DN191B LED 6S-6500 PSU WH S1) Wipro:LD35-400-XXX-50-XX Panasonic:ADL01R076 | BI01010001010000000000000515BI0100001237 | 10 | Nos. | 1258.13 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.024 | Supply and fixing of LED Tube light with batten suitable for up to 1 x 18 / 22 watt. LED plastic tube light, tube shall have 2100 lumen output complete including tube ect on surface complete in all respects. (Philips Cat no. TMC 501 P 1X T-LED 22W P3241) Wipro :LL20-551-XXX-60-XX LL13-181-65 Panasonic:ABT021206 | BI01010001010000000000000515BI0100001238 | 182 | Nos | 1289.19 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.025 | SECTION - VI : CABLE AND CABLE TRAYS Supply of following sizes of XLPE insulated PVC sheathed Aluminium / copper conductor armoured cable of 1.1 KV grade on existing cable tray / trench / surface including saddle, clamps etc. complete as required. 4.0 Core X 25 Sqmm. | BI01010001010000000000000515BI0100001239 | 100 | Mtr. | 250.97 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.026 | SECTION - VI : CABLE AND CABLE TRAYS Supply of following sizes of XLPE insulated PVC sheathed Aluminium / copper conductor armoured cable of 1.1 KV grade on existing cable tray / trench / surface including saddle, clamps etc. complete as required. 3½ Core X 95 Sqmm. | BI01010001010000000000000515BI0100001240 | 8.9 | Mtr. | 626.21 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.027 | Supply of thimbles of following types Copper Reducing type terminal/thimble | BI01010001010000000000000515BI0100001241 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.028 | 2.5 sq mm | BI01010001010000000000000515BI0100001242 | 70 | no. | 12.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.029 | 4 sq mm | BI01010001010000000000000515BI0100001243 | 200 | no. | 12.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.03 | 6 sq mm | BI01010001010000000000000515BI0100001244 | 15 | no. | 13.29 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.031 | 10 sq mm | BI01010001010000000000000515BI0100001245 | 50 | no. | 15.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.032 | 2.5 sq mm | BI01010001010000000000000515BI0100001246 | 70 | no. | 4.32 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.033 | 4 sq mm | BI01010001010000000000000515BI0100001247 | 200 | no. | 6.04 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.034 | 6 sq mm | BI01010001010000000000000515BI0100001248 | 15 | no. | 6.59 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.035 | 10 sq mm | BI01010001010000000000000515BI0100001249 | 50 | no. | 8.31 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.036 | 16 sq mm | BI01010001010000000000000515BI0100001250 | 16 | no. | 10.94 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.037 | Supplying and installing following size of perforated pre-painted M.S. Cable trays reducers with perforation not more than 17.5% jointed with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. 150 mm. Width x 50mm Depth x 1.6 mm Thickness | BI01010001010000000000000515BI0100001251 | 57.5 | Mtr. | 1102.81 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.038 | Supplying and installing following size of perforated pre-painted M.S. Cable trays reducers with perforation not more than 17.5% jointed with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. 200 mm. Width x 50mm Depth x 1.6 mm Thickness | BI01010001010000000000000515BI0100001252 | 7.2 | Mtr. | 1398.74 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.039 | Supplying and installing following size of perforated pre-painted M.S. Cable trays reducers with perforation not more than 17.5% jointed with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. 300 mm. Width x 50mm Depth x 1.6 mm Thickness | BI01010001010000000000000515BI0100001253 | 67.2 | Mtr. | 1702.04 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.04 | Providing and Fixing 25mm X 5mm G.I. Strip on surface or in recess for connections etc. as required. | BI01010001010000000000000515BI0100001254 | 22 | Rmt | 116.09 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.041 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | BI01010001010000000000000515BI0100001255 | 768 | Rmt | 28.61 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.042 | AIR COOLED DUCTABLE SPLIT AIR CONDITIONER Supply, installation, testing, commissioning and handing over the following equipment, schedule and drawings, all complete as required.Self Contained Air Cooled type Ductable split units system, complete with Scroll Compressor, motor, multi-row deep copper cooling coil with aluminum fins, multi -row deep air cooled condenser with copper tubes and aluminum fins, condenser fan. Indoor fan section with blower, fan motor and filters. The mounting of fan & motor shall be isolated from unit body by means of vibration isolators. The unit shall be in two parts i.e. indoor units and outdoor units complete with interconnecting copper refrigerant piping & insulation, electrical power & control wiring between unit panel, indoor and outdoor unit, safeties, controls etc. Type of Unit: Compressor shall be Hermetically sealed Scroll type working on Refrigerant R-22 OUTDOOR UNIT Supply, installation, testing and commissioning of out door units complete with scroll compressors , air cooled condenser with low noise fan having interconnected control wiring and refrigerant piping housed in compact housing duly powder coated of following capacities.Capacity : 5.5 TR Indoor units Supply, installation, testing and commissioning of indoor units with evaporator coil with Blower, Motor, filters & drain pump, to dispose the condensate drain to the nearest drain.- 1 Nos. The indoor units shall be complete with corded remote Capacity : 11.0 TR -2 Nos. Indoor units Supply, installation, testing and commissioning of indoor units with evaporator coil with Blower, Motor, filters & drain pump, to dispose the condensate drain to the nearest drain. The indoor units shall be complete with corded remote Capacity : 8.5 TR -2 Nos. | BI01010001010000000000000515BI0100001256 | 1 | Nos. | 100753.61 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.043 | AIR COOLED DUCTABLE SPLIT AIR CONDITIONER Supply, installation, testing, commissioning and handing over the following equipment, schedule and drawings, all complete as required.Self Contained Air Cooled type Ductable split units system, complete with Scroll Compressor, motor, multi-row deep copper cooling coil with aluminum fins, multi -row deep air cooled condenser with copper tubes and aluminum fins, condenser fan. Indoor fan section with blower, fan motor and filters. The mounting of fan & motor shall be isolated from unit body by means of vibration isolators. The unit shall be in two parts i.e. indoor units and outdoor units complete with interconnecting copper refrigerant piping & insulation, electrical power & control wiring between unit panel, indoor and outdoor unit, safeties, controls etc. Type of Unit: Compressor shall be Hermetically sealed Scroll type working on Refrigerant R-22 OUTDOOR UNIT Supply, installation, testing and commissioning of out door units complete with scroll compressors , air cooled condenser with low noise fan having interconnected control wiring and refrigerant piping housed in compact housing duly powder coated of following capacities. Capacity : 11.0 TR | BI01010001010000000000000515BI0100001257 | 2 | Nos. | 172611.86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.044 | AIR COOLED DUCTABLE SPLIT AIR CONDITIONER Supply, installation, testing, commissioning and handing over the following equipment, schedule and drawings, all complete as required.Self Contained Air Cooled type Ductable split units system, complete with Scroll Compressor, motor, multi-row deep copper cooling coil with aluminum fins, multi -row deep air cooled condenser with copper tubes and aluminum fins, condenser fan. Indoor fan section with blower, fan motor and filters. The mounting of fan & motor shall be isolated from unit body by means of vibration isolators. The unit shall be in two parts i.e. indoor units and outdoor units complete with interconnecting copper refrigerant piping & insulation, electrical power & control wiring between unit panel, indoor and outdoor unit, safeties, controls etc. Type of Unit: Compressor shall be Hermetically sealed Scroll type working on Refrigerant R-22 OUTDOOR UNIT Supply, installation, testing and commissioning of out door units complete with scroll compressors , air cooled condenser with low noise fan having interconnected control wiring and refrigerant piping housed in compact housing duly powder coated of following capacities. Capacity : 8.5 TR | BI01010001010000000000000515BI0100001258 | 2 | Nos. | 131288.87 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.045 | Note : Cost of Refrigerant / gas filling & charging for above units as per standard requirement for proper working is included in the above price. Refrigerant PipingSupply, installation and Testing & commissioning copper refrigerant piping to interconnect indoor unit and outdoor unit and routing the piping through the shaft / ceiling as shown in the drawing. Refrigerant piping shall be insulated complete with (19mm/13mm thick) closed cell elastomeric nitrile rubber tubular between each set of indoor & outdoor units, all the piping inside shall be properly supported with GI hanger. Size for 8.5TR unit:- (Suction:-11/8" and Liquid:-5/8") | BI01010001010000000000000515BI0100001259 | 25.19 | Rmts. | 1446.98 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.046 | Note : Cost of Refrigerant / gas filling & charging for above units as per standard requirement for proper working is included in the above price. Refrigerant PipingSupply, installation and Testing & commissioning copper refrigerant piping to interconnect indoor unit and outdoor unit and routing the piping through the shaft / ceiling as shown in the drawing. Refrigerant piping shall be insulated complete with (19mm/13mm thick) closed cell elastomeric nitrile rubber tubular between each set of indoor & outdoor units, all the piping inside shall be properly supported with GI hanger. Size for 5.5TR unit:- (Suction:-7/8" and Liquid:-5/8") | BI01010001010000000000000515BI0100001260 | 66 | Rmts. | 1249.96 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.047 | Note : Cost of Refrigerant / gas filling & charging for above units as per standard requirement for proper working is included in the above price. Refrigerant PipingSupply, installation and Testing & commissioning copper refrigerant piping to interconnect indoor unit and outdoor unit and routing the piping through the shaft / ceiling as shown in the drawing. Refrigerant piping shall be insulated complete with (19mm/13mm thick) closed cell elastomeric nitrile rubber tubular between each set of indoor & outdoor units, all the piping inside shall be properly supported with GI hanger. Size for 1.5TR unit:- (Suction:-1/2" and Liquid:-1/4") | BI01010001010000000000000515BI0100001261 | 43.4 | Rmts. | 788.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.048 | ( Quantity considered is 10 Rmt per unit ) Control and Power cablesSupply, installation,testing and commissioing of power/ control cables of PVC sheathed flexible copper wire complete with earthing between indoor and outdoor units. All external cables shall run in cable trays. | BI01010001010000000000000515BI0100001262 | 5 | Nos. | 41628.74 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.049 | Note : Cost of Refrigerant / gas filling & charging for above units as per standard requirement for proper working is included in the above price. AUTOMATIC VOLTAGE STABILIZER Supply, Installation, testing and commissioning of AUTOMATIC VOLTAGE STABILIZER with 3 step relay to covert 140-280 volts incoming power to 200-240 volts out going power, low/high voltage cutout, time delay relay, digital display of voltage / current. Voltage stabilizer 4 KVA for 1.5 TR, (wall mounted type) | BI01010001010000000000000515BI0100001263 | 5 | Nos. | 2401 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.05 | Base stand for outdoor unit fabricated out of 40 x 40 x 5 mm angle iron frame duly painted with black enamel paint | BI01010001010000000000000515BI0100001264 | 8 | Nos. | 2043.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.051 | Drain Piping Supply, installation and Testing & commissioning of rigid heavy duty PVC piping complete with fittings, supports and duly insulated with 6 mm thick closed cell nitrile rubber insulation. 32 MM DIA | BI01010001010000000000000515BI0100001265 | 67 | Rmts. | 297.57 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.052 | Drain Piping Supply, installation and Testing & commissioning of rigid heavy duty PVC piping complete with fittings, supports and duly insulated with 6 mm thick closed cell nitrile rubber insulation. 25 MM DIA | BI01010001010000000000000515BI0100001266 | 27.5 | Rmts. | 261.6 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.053 | ( Quantity considered is 6 Rmt per unit ) AIR DISTRIBUTION Site Fabricated duct Supply, fabrication, installation and testing of sheet metal ducts including necessary supporting arrangement in accordance with the approved shop drawings and as per the specifications: 24 G (0.63 mm) | BI01010001010000000000000515BI0100001267 | 168.79 | sqm. | 494.59 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.054 | ( Quantity considered is 6 Rmt per unit ) AIR DISTRIBUTION Site Fabricated duct Supply, fabrication, installation and testing of sheet metal ducts including necessary supporting arrangement in accordance with the approved shop drawings and as per the specifications: 22 G (0.8 mm) | BI01010001010000000000000515BI0100001268 | 30 | sqm. | 595.14 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.055 | DIFFUSERS SUPPLY AIR DIFFUSERS 'Supply,Installatio, Testing and commissioning of square supply air diffusers as per approved shop floor drawings and colour. Each diffuser will be equipped with removable core and an AL volume control damper which will be key operated. Powder coated extruded aluminium supply air diffuser of approved colour and shade. | BI01010001010000000000000515BI0100001269 | 1.5 | sqm. | 7080.37 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.056 | RETURN AIR DIFFUSER 'Supply,Installation, Testing and commissioning of square return air diffusers as per approved shop floor drawings and colour. Each diffuser will be equipped with removable core . Powder coated extruded aluminium exhaust air diffuser of approved colour and shade. | BI01010001010000000000000515BI0100001270 | 1.5 | sqm. | 4573.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.057 | GRILLS Supply, installation, testing and commissioning of extruded aluminium powder coated supply air grills of approved shade and make. Supply, installation, testing and balancing of one way blow linear supply cum return air grills as per approved shop drawings and specifications. The grills shall be of approved colour and shade. Powder coated aluminium grills of extruded sections with integral flanges on both sides and ends as required. 150mm high | BI01010001010000000000000515BI0100001271 | 3.5 | sqm. | 5809.97 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.058 | VOLUME CONTROL DAMPERS Supply, Installation and Testing of multiblade box type GSS construction damper for ducts, to be provided with suitable links and quadrants for control of volume of air. | BI01010001010000000000000515BI0100001272 | 1.5 | sqm. | 4425.13 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.059 | Supply, installation, testing and commissioning of extruded aluminium powder coated grills. Extruded aluminium construction, single louvered, powder coated grille for return air. | BI01010001010000000000000515BI0100001273 | 18 | Sqm | 3302.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.06 | THERMAL INSULATION ( for site fabricated ducts) AC duct Supplying and fixing of following thickness duly laminated aluminium foil of mat fininshed closed cell Nitrile rubber (class ''O'') insulation on duct after applying two coats of cold setting adhesive (The joints shall sealed with 50mm wide and 3 mm thick self adhesive nitrile rubber tape insulaton complete as per specifications and as required. 19 mm thick insulation for supply air duct in AC area. | BI01010001010000000000000515BI0100001274 | 161.24 | SqM | 667.08 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.061 | Supply and fixing of acoustic lining of supply air duct and plenum with 25 mm thick resin bonded glass wool having density of 32 kg/m³, with 25 mm X 25 mm GI section of 1.25 mm thick, at 600 mm centre to centre covered with Reinforced Plastic tissue paper and 0.5 mm thick perforated aluminum sheet fixed to inside surface of ducts with cadmium plated nuts, bolts, stick pins, CPRX compound etc. complete as required and as per specifications. 25 mm thick | BI01010001010000000000000515BI0100001275 | 10 | Sqm. | 443.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.062 | P/F Hand Dryer(Electrical work)as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001276 | 4 | Each | 8122.19 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.063 | Core Cutting Driiling , Size 63mmx350mm deep. | BI01010001010000000000000515BI0100001277 | 5 | Each | 4117.53 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.064 | Core Cutting Driiling , Size 125mmx350mm deep. as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001278 | 1 | Each | 5646.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.065 | Providing and fixing of Fixing of Aluminium Anodised Imported Profile in the size of 70mm wide overall with acrelick milky difuser, end cap and spring for fixing arrangement with Osram/Panasonic make 48 watt LED Strip per 5 mtr 4000 k…….Make is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001279 | 52 | Mtr. | 2771.92 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.066 | Supply, fabrication, installation and testing of the flexible connections constructed out of fire resistant double canvas sleeve as per the approved shop drawingsMake is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001280 | 5 | Each | 5669.84 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.067 | Providing and fixing Electric Geyser capacity 25 l with inlet and pot let connection appoved quality omplete and making good the wall where required. Make is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001281 | 4 | Each | 11969.66 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.068 | Supply and installation of Inline Fans for Pantry and Toilet Exhaust with double canvass connection, support, etc.Make is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001282 | 1 | Each | 44098.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.069 | Supply, laying, testing and commissoning of 1100V grade armoured/Unarmoured cable having sector/circular shaped copper conductor PVC insulated cores under ground PVC tape….. of 1X25SQM Copper CableMake is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001283 | 20 | Rmt. | 243.93 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.07 | Supply, laying, testing and commissoning of 1100V grade Unarmoured cable having sector/circular shaped copper conductor PVC insulated cores under ground PVC tape….. of 4CX4 SQM Copper Cable | BI01010001010000000000000515BI0100001284 | 99.8 | Rmt. | 180.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.071 | Supply, laying, testing and commissoning of 1100V grade Unarmoured cable having sector/circular shaped copper conductor PVC insulated cores under ground PVC tape….. of 4CX6 Sqm Copper CableMake is as per direction of Engineer-in-charge\ | BI01010001010000000000000515BI0100001285 | 290 | Rmt. | 240.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.072 | SITC of 2 TR Cassette AC as per the site requirment, complete in all respect as per the direction of Enginner in Charge | BI01010001010000000000000515BI0100001286 | 1 | Each. | 81897.69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.073 | Interconnecting R410A refrigerant pipe work with (13 mm thick) closed cell elMake is as per direction of Engineer-in-chargeastomeric nitrile rubber tubular insulation between each set of indoor & outdoor units as per specifications, all piping inside the room shall be properly supported…. | BI01010001010000000000000515BI0100001287 | 7 | Rmt. | 1239.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.074 | Providing & fixing control cum transmission wiring of 3 core x 2.5 sq mm copper of following size on cable tray as required between indoor and out door unit. | BI01010001010000000000000515BI0100001288 | 7 | Rmt. | 109.05 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.075 | Providing & fixing of MS Frame wall mounted stand.Make is as per direction of Engineer-in-charge | BI01010001010000000000000515BI0100001289 | 1 | Each. | 4435.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.076 | Supply, laying, testing and commissoning of 1100V grade PVC armoured cable 4.0 Core X 10 Sqmm. copper Cable. | BI01010001010000000000000515BI0100001290 | 290 | Rmt. | 399.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.077 | Supply, laying, testing and commissoning of 1100V grade PVC armoured cable 4.0 Core X 16SQM copper Cable. | BI01010001010000000000000515BI0100001291 | 110 | Rmt. | 560.79 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.078 | Supplying, Fixing,testing and commissioning of fire dampers in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring,the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications. | BI01010001010000000000000515BI0100001292 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.079 | Fire damper | BI01010001010000000000000515BI0100001293 | 2 | sqm | 5766 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.08 | Actuator | BI01010001010000000000000515BI0100001294 | 5 | Each | 5355 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.081 | Supply and fixing of 36 Watt to 46 Watt indoor Recess mounting LED Square Fitting for Armstrong Ceiling having Powder coated die cast aluminium housing body with extended heat sink and diffuser of Special Polycarbonate meterial and driver set complete in all respect. CAT-AAA | BI01010001010000000000000515BI0100001295 | 28 | Each | 5756 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.082 | Supply and fixing of decorative 8 to 16 Watt LED bollard luminaire with driver set confirming to IP 65 protection complete in all respect | BI01010001010000000000000515BI0100001296 | 6 | Each | 3327 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.083 | Supply and fixing of call bell/Buzzer suitable for singal phase, 230V complete as required. | BI01010001010000000000000515BI0100001297 | 5 | Each | 75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.084 | Supply and fixing 63 Amp. 4 pole MCB(10 KA) C Curve | BI01010001010000000000000515BI0100001298 | 3 | Nos. | 1872 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.085 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | BI01010001010000000000000515BI0100001299 | 51 | Mtr. | 86.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.086 | Supply, installation, testing and commissioning of 1HP Pressure pump connected to tank, cable etc. , complete in all respect. | BI01010001010000000000000515BI0100001300 | 1 | Each | 22292 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.087 | Supply and fixing of exhaust fan and complete in all respect. | BI01010001010000000000000515BI0100001301 | 8 | Each | 2577 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.088 | Supply and fixing of 12 watt LED Spot/Spike light luminaire Confirming to IP 65 Protection complete in all respect. | BI01010001010000000000000515BI0100001302 | 12 | Each | 2508 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.089 | Supply and fixing of 12 w step light , complete in all respect. | BI01010001010000000000000515BI0100001303 | 4 | Each | 1672 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.09 | Supply and fixing of lantern light, complete in all respect. | BI01010001010000000000000515BI0100001304 | 4 | Each | 4180 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.091 | Supply and fixing weather proof shocket , complete in all respect. | BI01010001010000000000000515BI0100001305 | 2 | Each | 2090 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.092 | Supply and fixing of wall washer light, complete in all respect. | BI01010001010000000000000515BI0100001306 | 4 | Each | 2508 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.093 | Providing and fixing of IP65 BOX for fountain starter motor | BI01010001010000000000000515BI0100001307 | 4 | Nos. | 7744 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.094 | Providing and fixing of SS-304 grade stainless steel brush finish sheet for electrical junction box in various size | BI01010001010000000000000515BI0100001308 | 200 | SQINCH | 15 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.095 | FIRE ALARM | BI01010001010000000000000515BI0100001309 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.096 | PHOTOTHERMAL (MULTITECH) DETECTOR | BI01010001010000000000000515BI0100001310 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.097 | Supply, Installation, Testing & Commissioning, Installation of UL listed Intelligent Addressable MultiCriteria smoke cum Heat detector, optical type with blinking LED and standard base, being capable of being addressed electronically. Manual Addressing not acceptable. complete with base etc. as required. Approved Make:-Notifier/Ansul/Edwards | BI01010001010000000000000515BI0100001311 | 35 | Nos. | 4661.86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.098 | FAULT ISOLATOR | BI01010001010000000000000515BI0100001312 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.099 | Supply, Installation, Testing & Commissioning of UL Listed Addressable Fault Isolator module complete which detects short circuit and seperates the segment, complete etc. as required.and as per specifications.Approved Make:-Notifier/Ansul/Edwards | BI01010001010000000000000515BI0100001313 | 2 | Nos. | 4035.64 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.1 | CONTROL MODULES | BI01010001010000000000000515BI0100001314 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.101 | Supply of UL Listed Addressable control module (MCP) complete as required for switching ON of smoke extraction fans / Pressurisation Fans etc. and switching off AHU' s, capable of being addressed electronically. Manual Addressing (Dip/ Rotary Switches) not acceptable, complete as required.and as per specifications. Sprinkler flow switches. Approved Make:-Notifier/Ansul/Edwards | BI01010001010000000000000515BI0100001315 | 2 | RO | 4610.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.102 | MONITOR MODULES | BI01010001010000000000000515BI0100001316 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.103 | Supply, Installation, Testing & Commissioning of UL Listed Addressable Monitor module complete as required for monitoring flow switches/ interface with any third party equipment capable of being addressed electronically etc. completeas required and as per specifications Hooters Circuit.Approved Make:-Notifier/Ansul/Edwards | BI01010001010000000000000515BI0100001317 | 1 | Nos | 4377.66 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.104 | Suppluing abd Installation , of exit signs: photo luminescent safety signage made up of photo luminescent material of rare earth aluminates, non radioactive working. | BI01010001010000000000000515BI0100001318 | 3 | Nos | 372.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.105 | CABLES | BI01010001010000000000000515BI0100001319 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.106 | Supply, Installation, Testing & Commissioning of PVC Insulated 2 x 1.5 sq mm FRLS copper conductor flexible cable with termination on each end with ferrules .Approved Make:-Polycab/Customized/Parashield | BI01010001010000000000000515BI0100001320 | 450 | RM | 119.56 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.107 | Response Indicator. Approved Make:-Notifier/Edwards/Ansul | BI01010001010000000000000515BI0100001321 | 4 | Nos. | 122.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.108 | HEAT DETECTOR | BI01010001010000000000000515BI0100001322 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.109 | Supply, installing, testing and commissioning of UL Listed Addressable Rate of Rise Heat Detector rated at 9.4 deg C/min. The detector shall have twin bi-colour LED for 360 deg viewing. Addressing shall be with user friendly rotary decimal switches. Approved Make:-Notifier/Edwards/Ansul | BI01010001010000000000000515BI0100001323 | 4 | Nos. | 3992.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.11 | SPEAKERS | BI01010001010000000000000515BI0100001324 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.111 | Supply, installing, testing and commissioning ofUL Listed 2W/6W Ceiling Mounted speaker with capacity to have 1/4,1/2,1 and 2 watt tapping, working at 83dB compatible with amplifier complete as required. Approved Make:-Honeywell/Bosch/Ateis | BI01010001010000000000000515BI0100001325 | 16 | Nos. | 2590.14 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.112 | Fire Hydrant System | BI01010001010000000000000515BI0100001326 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.113 | Providing, fixing, testing & commissioning of MS air cushion tank on top of each riser fabricated from 6mm thick MS plate, 200 mm in diameter and 1.2 m in height with dished ends fabricated from 8mm thick MS plate with Air release valve with stop cock, flanged inlet connection and drain arrangement with 25mm dia valve, pressure gauge with gun metal stop cock complete with all accessories as required and conforming to IS 4736-1968. (The cushion tank should be suitable for rated working pressure. (Make: SafeFire, Radiant, East West) | BI01010001010000000000000515BI0100001327 | 2 | set | 7303.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.114 | Providing & fixing dial type (100 mm) pressure gauge with isolation ball valve suitable for working pressure of 250 PSI. Cost shall be inclusive of providing any short pieces, nipples, elbows etc as required. | BI01010001010000000000000515BI0100001328 | 3 | Nos | 777.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.115 | SUBHEAD: II: Hydrants, Sprinkler,Piping & Accessories | BI01010001010000000000000515BI0100001329 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.116 | Supplying, laying, fixing, testing and commissioning of following sizes (NB) of ISI marked heavy class M.S. pipes including cutting, threading, welding etc. and providing all victaulic fittings e.g. elbows, reducers, clamps, hangers, flanges, gaskets, nuts, bolts and washers etc. including painting of pipes and fittings with red paint over a coat of ready mixed primer, both of approved quality and shade including cutting holes and chases in brick or RCC walls/slabs and making good the same etc. complete in all respect as required. (Make: Tata , Radiant , Jindal) | BI01010001010000000000000515BI0100001330 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.117 | 150 mm dia | BI01010001010000000000000515BI0100001331 | 50 | Metre | 1981.11 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.118 | 100 mm dia | BI01010001010000000000000515BI0100001332 | 22.25 | Metre | 1430.99 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.119 | 80 mm dia | BI01010001010000000000000515BI0100001333 | 14 | Metre | 1050.88 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.12 | 65 mm dia | BI01010001010000000000000515BI0100001334 | 15 | Metre | 918.15 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.121 | 50 mm dia | BI01010001010000000000000515BI0100001335 | 15.75 | Metre | 762.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.122 | 40 mm dia | BI01010001010000000000000515BI0100001336 | 23.25 | Metre | 609.36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.123 | 32 mm dia | BI01010001010000000000000515BI0100001337 | 10.5 | Metre | 560.47 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.124 | 25 mm dia | BI01010001010000000000000515BI0100001338 | 107.75 | Metre | 492.32 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.125 | Providing and fixing forged brass ball valve with forged brass ball (suitable for test pressure of not less than 15 kg / sq.cm of the following size : (Make: Zoloto, AIP, Sant) (Cost shall be inclusive of providing necessary union / flange connection). | BI01010001010000000000000515BI0100001339 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.126 | 25 mm dia | BI01010001010000000000000515BI0100001340 | 1 | No. | 959.36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.127 | Providing & fixing of butterfly valve (suitable for test pressure of 15 kg / sqm) with flanges, nut bolts, gaskets and necessary pad locking arrangement complete required. (Make: Zoloto, AIP, Sant) | BI01010001010000000000000515BI0100001341 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.128 | 80 mm dia | BI01010001010000000000000515BI0100001342 | 1 | No. | 2945.02 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.129 | 100 mm dia | BI01010001010000000000000515BI0100001343 | 2 | No. | 3762.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.13 | 150 mm dia | BI01010001010000000000000515BI0100001344 | 1 | No. | 5668.61 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.131 | Providing & fixing swinging type First Aid hose reel in red colour drum with 30 mts long and 20 mm dia heavy duty rubber water hose, 20 mm dia globe valve stop cock, terminating with G.M. coupling & nozzle of 6mm outlet with shut off valve confirming to IS 8090 - 1976 complete with MS socket for tap-off, drum and brackets (including painting) for fixing on wall with anchor fastner, bolts & nuts conforming to IS:884-1969 complete as required.(Make: Radiant, East West,Padmani, Zoloto) | BI01010001010000000000000515BI0100001345 | 1 | No. | 6243.44 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.132 | Providing & fixing non-percolating rubber reinforced lined fire hose pipe (as per IS : 636) of 63 mm dia and length as described below. The hose shall be rated for brust pressure of 35.7 Kg/sqcm. Hose shall be complete with ISI marked S.S male & female coupling (IS:903) bound & rivetted to hose pipe with copper rivets & 1.5 mm copper wire (Location : Internal fire hydrant) (Make: Radiant, East West,Padmani,) | BI01010001010000000000000515BI0100001346 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.133 | 15 m length | BI01010001010000000000000515BI0100001347 | 2 | Nos | 4712.03 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.134 | Providing and Fixing 63 mm dia instantaneous pattern branch short Stainless Steel pipe, 20 mm dia nozzle conforming to IS 903, suitable for inter connection to hose pipe coupling complete as required.(Make: Radiant,Padmani,kartar,) | BI01010001010000000000000515BI0100001348 | 2 | Nos | 2462.04 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.135 | Providing and fixing standard fire man's axe with heavy rubber handle.(Make: Radiant, East West,Padmani) | BI01010001010000000000000515BI0100001349 | 1 | Nos | 559.56 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.136 | Providing and fixing 5 mm thick glass door (with M.S. frame) of size 2.1 m x 1.2 m with center opening for fire hose cabinet. Suitably marked on the outside with the letters "FIRE HOSE" including locking arrangement. All M.S. work to be in Red P.O. colour over appropriate primer. The above item is only for masonary fire station.(Make: Radiant, East West,Padmani) | BI01010001010000000000000515BI0100001350 | 2 | No. | 9541.86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.137 | Providing and fixing flexible connectors consisting of flexible core 1.5 mtr. in lenghth of corrugated stainless steel tubing under the braid, (Braiding to be SS-304, tubing to be SS-304) for minimum working pressure rating of 200 PSI to be installed at connections from branch pipes to pendant sprinklers blow false ceiling as per specification of the manufacturers. (Make: Radiant, East West,Padmani) | BI01010001010000000000000515BI0100001351 | 70 | Nos | 902.83 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.138 | Providing and Fixing 15 mm dia gunmetal / brass quartzoid type Sprinkler Head with quartz bulb and set to operate at specified temperature.(Make:East West,Padmani) | BI01010001010000000000000515BI0100001352 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.139 | Pendant Type,68° C, Chrome plated | BI01010001010000000000000515BI0100001353 | 70 | Nos | 240.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.14 | SUBHEAD: III: Portable Chemical Fire Extinguishers | BI01010001010000000000000515BI0100001354 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.141 | Supply, installation, testing and commissioning of following types of extinguisher with provision of wall bracket (fixed with anchor fastner). | BI01010001010000000000000515BI0100001355 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.142 | ISI marked (IS:940) portable chemical fire extinguisher, water (gas pressure) type capacity 9 litres with gun metal cap and nozzle and complete in all respects including initial fill and wall suspension brackets(Make: East West,Padmani) | BI01010001010000000000000515BI0100001356 | 5 | Each | 3534.02 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.143 | ISI marked (IS:2878) Fire Extinguisher, Carbon-di-oxide type capacity 4.5 Kg. Flat base including valve, discharge hose of not less than 10 mm dia, 1M long and complete in all respects including initial fill with CO2 gas conforming to IS:307-1966 filled to a filling rate of not more than 0.667 and wall suspension bracket.(Make: East West,Padmani) | BI01010001010000000000000515BI0100001357 | 3 | Each | 6007.84 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.144 | ISI marked (IS:2171) Portable Dry Chemical Power Type Fire Extinguisher with Gun Metal cap and nozzle and complete in all respects including initial fill and wall suspension bracket(Make: East West,Padmani) | BI01010001010000000000000515BI0100001358 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.145 | 5 Kg | BI01010001010000000000000515BI0100001359 | 3 | Each | 3239.52 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.146 | Lift | BI01010001010000000000000515BI0100001360 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.147 | Supply of items, repairs and annual maintenance of MD lift parts make kone & equivalent | BI01010001010000000000000515BI0100001361 | 1 | Set | 292667 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.148 | 65inch LED TV Make LG, SONY, Samsung 4k, UHD smart TV with Installation | BI01010001010000000000000515BI0100001362 | 1 | Nos. | 178203.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | SCHDEULE C (TELECOM WORKS) | BI01010001010000000000000515BI0100001363 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.001 | Supply installation testing and commissioning of following telephone instruments as per technical specification and as required. Digital Insturments with 12 Button Programable Digital Phone | BI01010001010000000000000515BI0100001364 | 28 | Each | 12722.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.002 | Supply installation testing and commissioning of following telephone instruments as per technical specification and as required. Analog CLI Normal Phone | BI01010001010000000000000515BI0100001365 | 52 | Each | 1170.66 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.003 | Supply and Installation of 100 Pair MDF with Housing | BI01010001010000000000000515BI0100001366 | 1 | Each | 13781.42 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.004 | Supply installation testing & Commissioning of intelligent Ethernet switch 24 Port RJ-45 Autosening 10/100/1000 Ports (EEE 802,3 Type 10 BASE-T LEEE 802.3u 100BASE-2SFP Fixed 1000 ports RJ 45 Serial console port support throughput minimum 84 gbps support advanced layer 2 feature should support POE power Budget 100W Should support zero touch deployment with india power cord make: Alcatel/ Net gear | BI01010001010000000000000515BI0100001367 | 6 | Each | 38677.56 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.005 | Supplying, Laying, Testing & Commissioning of Cat 6, PowerCat Plus ,UTP Cable, 4 pair, Blue (23 AWG, Reel in a Box packing) as per the requirement & complete in all respect and as directed to the satisfaction of engineer. Approved Make (Systimax / Molex / Penduit/D Link) | BI01010001010000000000000515BI0100001368 | 7000 | Mtr. | 26.98 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.006 | Supplying and fixing following size / modules, GI Box alongwith modular base & cover plate for modular siwtches in recess etc as required. 1 or 2 module ( 75mm x 75mm) | BI01010001010000000000000515BI0100001369 | 80 | Nos. | 135.71 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.007 | Supply and Fixing Folowing size/modules, GI Box along with modular base and Cover Plate for Modular switches in recess etc as required 1 or 2 module | BI01010001010000000000000515BI0100001370 | 80 | Nos. | 64.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.008 | Supply,Installation ,Testing and Commisioning of Single Port Iconable with RJ-45 I/O-White Preffered make D Link/ Systimax | BI01010001010000000000000515BI0100001371 | 80 | Nos. | 348.26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.009 | Supplying, Installation, Testing & Commissioning of Slime line RJ45 to RJ45 Cat6 UTP patchcord with flexible transparent Boot, Blue (Data Rack end) = 3 Feet, Preffered Make (Systimax / Molex / Penduit) | BI01010001010000000000000515BI0100001372 | 80 | Nos. | 285.31 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.01 | Supplying, Installation, Testing & Commissioning of Slime line RJ45 to RJ45 Cat6 UTP patchcord with flexible transparent Boot, Blue (Data Rack end) = 7 Feet, Preffered Make (Systimax / Molex / Penduit) | BI01010001010000000000000515BI0100001373 | 80 | Nos. | 327 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.011 | Supplying, Installation, Testing & Commissioning of 24 Port Cat 6 Straight Patch Panel, UTP 568A/B with Rear Cable Manager, 1U as per the requirement & complete in all respect and as directed to the satisfaction of engineer, Preffered Make (Systimax / Molex / Penduit) | BI01010001010000000000000515BI0100001374 | 6 | Nos. | 8414.53 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.012 | Supply installation testing & Commissioning armored multimode OFC cable 6 core unitube with two steel wire for interflow switch connectivity Preffered Make Digi –link/ Schneider/ AMP/ D- Link/ D -Link | BI01010001010000000000000515BI0100001375 | 100 | Nos. | 228.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.013 | Supply, installation, testing and commissioning of Data Rack 15 U (800mm * 800mm) free standing cabinet with front locable door, side panels, 2 set of castor wheel, 230V AC 90 CFM fan 4, three hardware packet 1set (containing 20Nos each of 3), AC Power strip combination of 5A - 15A 12 socket, heavy duty stationary shelf 600W x 475D, 2 cable channel 100mm wide 42U, one earthing strip 150mm H, 4 cable manager 1U height., Approved Make (Systimax / Molex / Penduit) | BI01010001010000000000000515BI0100001376 | 2 | Nos. | 8545.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.014 | Supply, laying, testing and commissoning of 1100V grade Unarmoured cable having sector/circular shaped copper conductor PVC insulated cores under ground PVC tape of 4CX4 SQM Copper Cable | BI01010001010000000000000515BI0100001377 | 99.8 | Nos. | 180.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Note on K13: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K114: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K141: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K192: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K209: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K210: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K212: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K214: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K216: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K219: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K222: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K224: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K226: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K229: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K230: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K239: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K241: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K246: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K252: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K254: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K255: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K258: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K260: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K263: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information