## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Noida Metro Rail Corporation (NMRC) Limited
Name of Work: Augmentation and Modification of Substation at Sector-137 metro station of NGN corridor Noida
Contract No:
Bidder Name :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE (Inclusive of all Taxes and Duties) In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | GENERAL DESCRIPTION | BI01010001010000000000000515BI0100001153 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.01 | Transformer should be type tested and the report should not be more than 5 years old. Transformer shall also comply with standards in force when the transformer is manufactured, particularly IEC 60076, Latest version, IS 2026; Latest version and IS 11171/1985. Maximum size available(L-2600mm, W-2000mm, H-2550mm) | BI01010001010000000000000515BI0100001154 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.02 | Augmenting existing LV Panel of M/s Neptune make, shall strictly be as per IEC-61439. The additional cubicle being made for housing 800 Amps, 415V ACB shall have Type tested design as per IEC-61439. The cubicle shall pass the internal arc fault containment test in accordance with IEC 61641 for fault current rating of 50 kA for 0.3 seconds. Panel augmentation & modification shall be minimum complying form 4b-type5 design. The colour of cubicle shall have the same RAL code as existing LV Panel. LT panel bus bar shall be capable of withholding the mentioned rated and fault current, the same shall be type tested as per IEC-61439 and temperature rise as per IEC 60890. | BI01010001010000000000000515BI0100001155 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.03 | Statutory sanctions such as E.I.G. clearance shall be under the scope of contractor. Application for grant of EIG shall be sent after performing the site test reports as per relevant IS/IEC. | BI01010001010000000000000515BI0100001156 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.04 | Type test certificate shall not be more than 5 year old of any equipment. | BI01010001010000000000000515BI0100001157 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.05 | The work/Equipment shall be in compliance of particular specification & BOQ. | BI01010001010000000000000515BI0100001158 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.06 | The manufacturing clearance of transformer shall be given after GTP approval by Engineer- in charge and dispatch clearance shall be given after satisfactory completion of FAT. | BI01010001010000000000000515BI0100001159 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.07 | The contractor shall submit the design documents for Augmentation of LV Panel such as GAD control wiring drawing and other relevant certificates. The augmentation clearance shall be given after approval of design documents. | BI01010001010000000000000515BI0100001160 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.08 | The contractor shall provide fault discrimination chart after augmenting LV Panel. | BI01010001010000000000000515BI0100001161 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2 | TRANSFORMER | BI01010001010000000000000515BI0100001114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.01 | SITC of Cast Resin Dry Type, 1000KVA, 33/0.415kV, 3 Phase, 50Hz, Dyn11 vector Group, Aluminium wound, Air Natural Cooling, Class F insulation associated with winding Temperature indicator/controller actuated by means of resistance temperature detector embedded in LV windings, indoor type Transformer with Approximately 6% impedance, OFF load tape changer, tapping on HV side in steps @0, +2.5% and +5% voltage range, having cable end termination on HV side suitable for 3X1Cx95 Sqmm copper XLPE cable of 33KV grade and LT Cable termination of 4Rx3.5Cx240Sqmm armoured Aluminium conductor cables on L.V. side with neutral bought out separately including supplying and laying of copper conductor multicore control cable from Transformer to HT Breaker for safety tripping and the magnetic circuit of transformer shall be in low loss oriented -grain silicon steel sheet. The connection with different terminals of transformer shall be through C-Type or suitable connector for sufficient clearances from transformer windings. HV connections of transformers shall be connected through insulated cables. HV terminals shall have suitable arrangement to provide sufficient clearance to 33 kV cables from the transformer windings. Transformer shall be fitted with a temperature protection system that allows winding temperatures to be monitored (this shall consist of two sensors placd on each low voltage winding; one alarm sensor and one trip out sensor). The transformer may be supplied in cubicle with enclosure without any HV portion exposed. The door shall be provided with a mechanical system interlock (Castle lock & key type). Transformer fire protection scheme shall cover supply, installation, testing and commissioning of automatic clean agent flooding system cosidering the following when computing volume to verify suitability and to establish design limitations complete for dry type transformer. *Volume of hazard area *Specific volume of clean agent *Discharge time and flow rates *Design concentration and design factors *detector/discharge tubing placement gas flooding of 4.2 percent cleaning agent concentration by volume as per NFPA- 2001 along with FACP and should have inetrface with main control fire alarm system. Approved make of transformer- M/s ABB / M/s RAYCHEM or equivalent. | BI01010001010000000000000515BI0100001115 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
2.02 | 1000KVA Transformer as described above | BI01010001010000000000000515BI0100001116 | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
3 | HT CABLES | BI01010001010000000000000515BI0100001117 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.01 | Supply & laying of 33 kV grade 3x1Cx95 sqmm Copper XLPE insulated PVC sheathed cable as per attached GTP. | BI01010001010000000000000515BI0100001118 | 30 | mtr |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3.02 | Termination of above cable at GIS end | BI01010001010000000000000515BI0100001119 | 3 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
3.03 | Termination of above cable at Transformer end | BI01010001010000000000000515BI0100001120 | 3 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
4 | MODIFICATION IN EXISTING MAIN DISTRIBUTION PANEL (INDOOR TYPE) - Neptune Make | BI01010001010000000000000515BI0100001121 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.01 | Incoming from Transformer (1000KVA) :- 1Nos. In existing enclosure. | BI01010001010000000000000515BI0100001122 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.02 | Supply, Installation, Testing & commissioning of 1Nos. 1600Amps., 415V, 50kA,4P with 100% neutral electrically operated draw out type, ACB complete with safety shutters, 240V AC shunt trip coil & closing coil and having microprocessor based (EMI & EMC Certified) with (1) Communication capability (2) Provision for measurement of three phase current (3) P{rotection against long time+ short time+earth fault (all with adjustable time delays) + instantaneous (4) Zone selective interlocking unit for total discrimination (5) Communication Options to remotely read and set parameters for the protections functions, Transmission of ameter measurements (6) Signalling of the cause of alarm & tripping, maximeter reset etc (7) 6NO+6NC contacts for interlock & indications (8) 1 no. of CT in the neutral to connect with the trip unit along with following items: | BI01010001010000000000000515BI0100001123 | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4.03 | 1Nos. Motor wound spring closing mechanism | BI01010001010000000000000515BI0100001124 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
4.04 | 1Nos. Microprocessor release PR122 (EMI & EMC Certified) for over current, earth fault & short circuit protection, instantaneous fault | BI01010001010000000000000515BI0100001125 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.05 | 3Nos. CT's for APFCR relay | BI01010001010000000000000515BI0100001126 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.06 | 1Nos. Undervoltage Release | BI01010001010000000000000515BI0100001127 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4.07 | Castle Lock & Key arrangement on Panel | BI01010001010000000000000515BI0100001128 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
4.08 | SCADA integration incorporating signals specified as per specifications. | BI01010001010000000000000515BI0100001129 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
4.09 | Existing multifunctional meter, APFCR relay, indication lamps, TNC switch, ALR switch, priority selector switch shall be used for metering & instrumentation purpose. | BI01010001010000000000000515BI0100001130 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5 | Shifting of Existing 800A ACB to New Enclosure | BI01010001010000000000000515BI0100001131 | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.01 | Installation, Testing & commissioning of new enclosure of size W600xH2125xD800 and shifting of existing 800A ACB with following accessories | BI01010001010000000000000515BI0100001132 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.02 | The cotractor shall also incorporate the existing clean agent based fire suppression system in its entire cubicle. | BI01010001010000000000000515BI0100001133 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.03 | 1Set. Phase indicating lamps suitable for 230 V AC fittings with back up hrc fuse/MCB. | BI01010001010000000000000515BI0100001134 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.04 | 4Nos. Breaker ON/OFF/TRIP/'Spring Charged', indicating lamps. | BI01010001010000000000000515BI0100001135 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.05 | 1Nos. T-N-C breaker control switch . (Trip/Neutral/Close) | BI01010001010000000000000515BI0100001136 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.06 | 3Nos. CT's for APFCR relay | BI01010001010000000000000515BI0100001137 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.07 | 1Nos. auto/Local/Remote selector switch | BI01010001010000000000000515BI0100001138 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.08 | 1Nos. Undervoltage Release | BI01010001010000000000000515BI0100001139 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.09 | 3 Nos. Metering CT (800/5A, CL-0.5, 15VA) | BI01010001010000000000000515BI0100001140 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.1 | SECURE/L&T make energy meter of 0.5s class | BI01010001010000000000000515BI0100001141 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.11 | Having provision for SCADA integration for signals as per specifications. | BI01010001010000000000000515BI0100001142 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
6 | Replacement of Horizontal Bus Bars | BI01010001010000000000000515BI0100001143 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
6.01 | Existing Tinned Copper Busbasr of 630A (size 2x40x10)mm shall be replaced with 1600A (Size 2 x 60x 10)mm for LHS part up to buscoupler section. Bus bars shall be colour coded and insulated by heat shrinkable sleaves & clip on shrouds for joints. | BI01010001010000000000000515BI0100001144 | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
6.02 | Note:- Work shall complete with interlocking of new Incoming Breaker with Buscoupler and Other incomer with necessory changes in control wiring. The existing LV panel is manufactured acc. To IEC 61439-1, the new cubical shall also having type tested certificate as per IEC 61439-1. | BI01010001010000000000000515BI0100001145 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
7 | LT CABLES: | BI01010001010000000000000515BI0100001146 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
7.01 | Supply and laying of 3.5C, 240 sqmm Aluminium XLPE insulated, 1100 V grade armoured FRLSH aluminium cable on existing cable tray including supports, clamps and dressing in all respect etc. | BI01010001010000000000000515BI0100001147 | 50 | mtr |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
7.02 | Supply & Termination of above cable having bimetallic lug (Cu-Al). | BI01010001010000000000000515BI0100001148 | 2 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
7.03 | Supply & Termination of above cable having Aluminium lug. | BI01010001010000000000000515BI0100001149 | 2 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
8 | EARTHING | BI01010001010000000000000515BI0100001150 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
8.01 | Providing and fixing of 50x6 sqmm GI flat strip for connection on surface or in recess for connections as required. | BI01010001010000000000000515BI0100001151 | 50 | mtr |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
9 | Dismantling existing 315kVA transformer and its transportation from Sec-137 metro station to RS depot. | BI01010001010000000000000515BI0100001152 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information